Verification report portable fire extinguishers & PbEG L 181

| No. | About | A | R | Remark | Result |
| --- | --- | --- | --- | --- | --- |
| 1 | Scope EN3-7+A1 | - | - |  |  |
| 2 | Normative references | - | - |  |  |
| 3 | Terms and definitions | - | - |  |  |
| 4.1 | Description of a portable fire extinguisher | A A | R R | Type Comp | C/N |
| 4.2 | Control of discharge | A | R |  | C/N |
| 4.3 | Operating position | A | R |  | C/N |
| 4.4 | Hose assembly | A | R |  | C/N |
| 4.5 | Propellants | A | R |  | C/N |
| 4.6 | Stored pressure extinguishers | A | R |  | C/N |
| 5 | Testing of portable fire extinguishers | A | R |  | C/N |
| 6 | Nominal charges, filling tolerances and minimum fire performance 1 Nominal charges (2) 2 Filling tolerances 3 Design of the filling opening, excluding carbon dioxide fire extinguishers (2) 4 Minimum fire ratings | A | R |  | C/N |
| 7 | Duration of operation, residual charge and operating temperatures 1 Duration of operation 2 Residual charge 3 Commencement of discharge 4 Effective range of operating temperature | A | R |  | C/N |
| 8 | Retention of propellants 1 Verification 2 Acceptance levels 3 Production leak tests | A | R |  | C/N |
| 9.1 9.2 | Dielectric test for water based extinguishers Required performance | A | R |  | C/N |
| 10.1 10.2 10.3 10.4 10.5 10.6 | Requirements for components Operation&emission control mechanisms/devices Safety devices Filter for water based portable fire extinguishers Hose and coupling systems Control valve | A | R |  | C/N |
| 11 | Means of pressure indication 1 Pressure gauge 2 Pressure indicator | A | R |  | C/N |
| 12 | Horns for carbon dioxide portable fire extinguishers | A | R |  | C/N |
| 13 | Portable fire extinguisher mounting bracket | A | R |  | C/N |
| 14 | Resistance to corrosion 1 Resistance to external corrosion 2 Resistance to extinguishing medium of extinguishers using water based media | A | R |  | C/N |
| 15 | Fire performance 2 Class A fire rating (14% moisture wood*) 3 Class B fire rating 4 Class F fire rating R Class D fire rating according NEN 2033 *a report according BS6165 is not accepted. | A | R |  | C/N |
| 16 | Portable fire extinguisher identification 1 Colour (red); 2 Marking; Part 1 the words ‘FIRE EXTINGUISHER’ or ‘EXTINGUISHER’ plus medium, or ‘FIRE EXTINGUISHER’ plus medium; Part 1 the type of extinguishing medium and the nominal charge; Part 1 the fire rating or ratings of the extinguisher; Part 2 User instruction and fire classes; Part 3 Safety instructions; electrical & toxicity risk(s) H9.2; Part 4 Refill and maintenance instructions; Part 4 an instruction to refill after any operation; Part 4 an instruction to check periodically and to use only products and spare parts in conformity with the agreed model for refilling and maintenance; Part 4 the identification of the extinguishing medium and, in particular, identification and percentage of additives for water based media; Part 4 if applicable, the identification of the propellant gas; Part 4 the number(s) or reference(s) relating to the approval of the extinguisher; Part 4 the manufacturer’s model designation; Part 4 the operating temperature range; Part 4 a warning against the risk of freezing for water based extinguishers; Part 4 a reference to the European Standard EN 3; Part 4 the periodic maintenance interval can be included in the marking given in Part 4 (see 16.2). NOTE 2 Attention is drawn to national regulations Part 5 Name and address MANUFACTURER; Part 5 In addition, the year of manufacture shall be marked somewhere on the portable fire extinguisher; RTK Transfer marking; RTK sub registration article 10; RTK = extra requirements based on the Dutch Approval Mark. | A | R |  | C/N |
| 17 | Maintenance; It shall be possible to perform periodic maintenance on each portable fire extinguisher. NOTE 1 The periodic maintenance interval can be included in the marking given in Part 4 (see 16.2). NOTE 2 Attention is drawn to national regulations. | A | R | Manufactures instructions in file at NCP | C/N |
| Annex | Normative | - | - |  | - |
| A B C D E F G H I J K L M | Duration of operation, residual charge tests Range of operating temperature Dielectric test Operation and emission control mechanisms/devices Test for performance of the hose Control valve test Tests on the horn Resistance to corrosion Fire tests Measurement of moisture content of wood Compaction procedure Specific requirements for Class F fire extinguisher Polar solvents |  |  |  | - |
|  | Testing report according to EN3-10 CEN-TR14922 - Ratings min 5A or 21B or 5F - Report is from a accepted Fire test lab | A | - R R | Lab; No; Date; | C |
|  | Construction Body according to - EN3-8 & PbEG L 181 | - A A | - RR | Lab; No; Date; | C/N |

A = applicable;  R = reported; C = conform; N = Not conform